## FloWatch Template
FloWatch Sprinkler Monitoring System Controller Point Schedule
[8 empty] | Project : |  |  | Project Name |  |  |  | Revision : | Draft
[8 empty] | Job Ref. : |  |  | Reference |  |  |  | Date : | 2020-04-03
[8 empty] | Design Eng. : |  |  | E.D.S. |  |  |  | Status : | Review
Module Ref |  |  | Input Channel | Signal Type | Terminals |  | Description | Field Device | FloWatch Software Name | Switch State (NO/NC) | Tag Ref | 100KΩ ( 'X' ) Series Resistor | 100KΩ ( 'Y' ) EOL Resistor | Tested | Date Test / Comissioned |  | Client Witness
Master Panel |  | Reception | Inputs
|  |  | 1 | v.f.c. | FL1 | GND | Ground Floor North Riser Sprinkler Flow Switch | Flow Switch |  | NO | FS/G | ü | ü | ü | 2020-05-23
|  |  | 2 | v.f.c. | FL2 | GND | Ground Floor North Riser Sprinkler Isolation Valve | Isolation Valve |  | NO | IV/G | ü | ü | ü | 2020-05-23
|  |  | 3 | v.f.c. | FL3 | GND | First Floor North Riser Sprinkler Flow Switch | Flow Switch |  | NO | FS/1 | ü | ü | ü | 2020-05-23
|  |  | 4 | v.f.c. | FL4 | GND | First Floor North Riser Sprinkler Isolation Valve | Isolation Valve |  | NO | IV/1 | ü | ü | ü | 2020-05-23
|  |  | 5 | v.f.c. | LL | GND | Sprinkler Storage Tank Low Level Alarm | Level Switch |  | NC | LS/1
|  |  | 6 | v.f.c. | PF | GND | Sprinkler Pump Set Common Alarm | Starter Panel vfc |  |  | ***
Outputs
|  |  |  | v.f.c. | FIRE | AL | Indication to Fire Alarm System | FAP / FIU |  |  | ***
|  |  |  | v.f.c. | BMS | BMS | Indication to Building Management System | BMS Panel |  |  | ***
Expansion Module | 0 | 1st Floor Riser | Inputs
|  |  | 1 | v.f.c. | IN1 | GND | Second Floor North Riser Sprinkler Flow Switch | Flow Switch |  | NO | FS/2 | ü | ü | ü | 2020-05-23
| Addresss |  | 2 | v.f.c. | IN2 | GND | Second Floor North Riser Sprinkler Isolation Valve | Isolation Valve |  | NC | IV/2 | ü | ü | ü | 2020-05-23
|  |  | 3 | v.f.c. | IN3 | GND | Spare Input
|  |  | 4 | v.f.c. | IN4 | GND | Spare Input
|  |  | 5 | v.f.c. | IN5 | GND | Spare Input
|  |  | 6 | v.f.c. | IN6 | GND | Spare Input
|  |  | 7 | v.f.c. | IN7 | GND | Spare Input
|  |  | 8 | v.f.c. | IN8 | GND | Spare Input
Expansion Module | 1 | Hallway | Inputs
|  |  | 1 | v.f.c. | IN1 | GND | Third Floor North Riser Sprinkler Flow Switch | Flow Switch |  | NO | FS/3 | ü | ü | ü | 2020-05-23
| Addresss |  | 2 | v.f.c. | IN2 | GND | Third Floor North Riser Sprinkler Isolation Valve | Isolation Valve |  | NC | IV/3 | ü | ü | ü | 2020-05-23
|  |  | 3 | v.f.c. | IN3 | GND | Spare Input
|  |  | 4 | v.f.c. | IN4 | GND | Spare Input
|  |  | 5 | v.f.c. | IN5 | GND | Spare Input
|  |  | 6 | v.f.c. | IN6 | GND | Spare Input
|  |  | 7 | v.f.c. | IN7 | GND | Spare Input
|  |  | 8 | v.f.c. | IN8 | GND | Spare Input
Expansion Module | 2 | Reception | Inputs
|  |  | 1 | v.f.c. | IN1 | GND | Fourth Floor North Riser Sprinkler Flow Switch | Flow Switch |  | NO | FS/4 | ü | ü | ü | 2020-05-23
| Addresss |  | 2 | v.f.c. | IN2 | GND | Fourth Floor North Riser Sprinkler Isolation Valve | Isolation Valve |  | NC | IV/4 | ü | ü | ü | 2020-05-23
|  |  | 3 | v.f.c. | IN3 | GND | Spare Input
|  |  | 4 | v.f.c. | IN4 | GND | Spare Input
|  |  | 5 | v.f.c. | IN5 | GND | Spare Input
|  |  | 6 | v.f.c. | IN6 | GND | Spare Input
|  |  | 7 | v.f.c. | IN7 | GND | Spare Input
|  |  | 8 | v.f.c. | IN8 | GND | Spare Input
Expansion Module | 3 | 6th Floor | Inputs
|  |  | 1 | v.f.c. | IN1 | GND | Fifth Floor North Riser Sprinkler Flow Switch | Flow Switch |  |  | FS/4 | ü | ü | ü | 2020-05-23
| Addresss |  | 2 | v.f.c. | IN2 | GND | Fifth Floor North Riser Sprinkler Isolation Valve | Isolation Valve |  |  | IV/4 | ü | ü | ü | 2020-05-23
|  |  | 3 | v.f.c. | IN3 | GND | Spare Input
|  |  | 4 | v.f.c. | IN4 | GND | Spare Input
|  |  | 5 | v.f.c. | IN5 | GND | Spare Input
|  |  | 6 | v.f.c. | IN6 | GND | Spare Input
|  |  | 7 | v.f.c. | IN7 | GND | Spare Input
|  |  | 8 | v.f.c. | IN8 | GND | Spare Input
Expansion Module | 4 | 6th Floor | Inputs
|  |  | 1 | v.f.c. | IN1 | GND | Fifth Floor North Riser Sprinkler Flow Switch | Flow Switch |  |  | FS/4 | ü | ü | ü | 2020-05-23
| Addresss |  | 2 | v.f.c. | IN2 | GND | Fifth Floor North Riser Sprinkler Isolation Valve | Isolation Valve |  |  | IV/4 | ü | ü | ü | 2020-05-23
|  |  | 3 | v.f.c. | IN3 | GND | Spare Input
|  |  | 4 | v.f.c. | IN4 | GND | Spare Input
|  |  | 5 | v.f.c. | IN5 | GND | Spare Input
|  |  | 6 | v.f.c. | IN6 | GND | Spare Input
|  |  | 7 | v.f.c. | IN7 | GND | Spare Input
|  |  | 8 | v.f.c. | IN8 | GND | Spare Input
Key
DO - Digital Output
v.f.c - Volt Free Contact
FloWatch Ltd
36 Ormside Way, Redhill, Surrey, RH1 2LW
Email: info@flowatch.co.uk www.flowatch.co.uk
Tel: 01737 481070